## R_H300E44-DA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBH / RFH
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2017-01-06 09:46
|  |  | Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
|  |  | Ambient |  | Saturated Suction Temperature (SST)
|  |  | Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F
|  |  | +90 Deg F |  | 27060 | 24730 | 22400 | 17760 | 15500 | 13300
|  |  | +95 Deg F |  | 25490 | 23260 | 21020 | 16560 | 14400 | 12310
|  |  | +100 Deg F |  | 24000 | 21820 | 19650 | 15390 | 13320 | 11330
|  |  | +105 Deg F |  | 22420 | 20370 | 18320 | 14230 | 12270 | 10380
|  |  | +110 Deg F |  | 20890 | 18940 | 16990 | 13110 | 11240 | 9460
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Hermetic |  | CS18K6E |  | 3 | 2 | 13.6 Lb's | 20.9 Lb's | 3.8 Lb's | 7.83 Lb's | 1/2" | 7/8" | 73 | 228 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 14.4 | 82 | 1 | 10 | 28 | 20 | 30 | 32.2 | 40
Notes: | + Applies to flooded head pressure control units only (model RFH) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A